## 能效指标
一级指标
| 指标名称 | 名称 | 单位 | 试验值 | 设计值 | 投产考核值 | 年统计值 | 华润年均值 | 华润先进 | 行业同类均值 | 行业同类先进值（20%） | 下限 | 上限 | 定义
供电煤耗 | 额定供电煤耗 | coal_consumption | g/kWh | 报告手填 | 可研手填 | 报告手填 | / | / | / | / | / | 200 | 400 | 产生1kWh电能消耗的标煤
| 年均供电煤耗 | Annual coal_consumption | g/kWh | 曲线拟合 | / | / | 年度月报自动 | 年度月报自动 | 年度月报自动 | 手填 | 手填
厂用电率 | 额定厂用电率 | Factory electricity rate | % | 报告手填 | 可研手填 | 报告手填 | / | / | / | / | / | 2 | 10 | 用于发电生产所消耗的电量占供电量比例
| 年均厂用电率 | Annual Factory electricity rate | % | 曲线拟合 | / | / | 年月报自动 | 年月报自动 | 年月报自动 | 手填 | 手填
| 油耗 | fuel_consumption_rate | t/a | / | / | / | 年月报手填 | 年月报手填 | 年月报手填 | 手填 | 手填 | 0 | 500 | 年消耗燃油量
| 水耗 | water_consumption_rate | kg/kWh | 报告手填 | 自动调用定额 | / | 年月报手填 | 年月报手填 | 年月报手填 | 手填 | 手填 | 0 | 5 | 产生1kWh电能消耗的水
二级指标
| 汽轮机热耗率 | heat rate | kJ/kWh | 报告手填 | 报告手填 | 报告手填 | 年月报自动 | 年月报自动 | 年月报自动 | / | / | 3600 | 9000 | 产生1kWh电能消耗的热量
| 锅炉效率 | boiler efficiency | % | 报告手填 | 报告手填 | 报告手填 | 年月报自动 | 年月报自动 | 年月报自动 | / | / | 80 | 100 | 锅炉利用热量的效率
三级指标
影响煤耗 | 主汽温度 | main_steam | ℃ | 报告手填 | 报告手填 | / | 年月报手填 | / | / | / | / | 500 | 650 | 汽轮机主汽门入口蒸汽温度
影响煤耗 | 再热温度 | reheat_steam | ℃ | 报告手填 | 报告手填 | / | 年月报手填 | / | / | / | / | 500 | 650 | 汽轮机中压主汽门入口蒸汽温度
影响煤耗 | 高压缸效率 | HP cylinder efficiency | % | 报告手填 | 报告手填 | 报告手填 | / | 年月报手填 | 年月报手填 | / | / | 75 | 100
影响煤耗 | 中压缸效率 | IP cylinder efficiency | % | 报告手填 | 报告手填 | 报告手填 | / | 年月报手填 | 年月报手填 | / | / | 75 | 100
影响煤耗 | 排烟温度 | exhaust temperature | ℃ | 报告手填 | 报告手填 | / | 年月报手填 | / | / | / | / | 90 | 200 | 空预器出口烟气温度
影响煤耗 | 空预器漏风 | wind leakage | % | 报告手填 | 报告手填 | / | 年月报手填 | / | / | / | / | 0 | 15
影响煤耗 | 灰渣含碳量 | carbon content of ash and clinker | % | 报告手填 | 报告手填 | / | 年月报手填 | / | / | / | / | 0 | 15
增加专业名词
Note on L4: Windows 用户: 数据来源：中电联报告
Note on L6: Windows 用户: 数据来源：中电联报告
Note on L7: Windows 用户: 数据来源：中电联报告
Note on L8: Windows 用户: 数据来源：中电联报告

## 变量名词
ID | name | 中文名称 | name | Name | 中文名称 | 来源 | 指标描述 | 上限 | 下限 | 单位 | 备注 | 类别 | name | 中文名称 | value
| power-plant-full-name | 电厂全称 | power plant full name | Power plant full name | 电厂全称 | 手填 | [6 empty] | power_plant_full_name | 电厂全称 | 华润电力焦作有限公司
| power-plant-abbreviated-name | 电厂简称 | power plant abbreviated name | Power plant abbreviated name | 电厂简称 | 手填 | [6 empty] | power_plant_abbreviated_name | 电厂简称 | 焦作项目
| unit-nums | 机组号 | unit nums | unit nums | 机组号 | 手填 | [6 empty] | unit_nums | 机组号 | 1号
|  | 0 | [11 empty] | 0
| rated-coal-consumption-test-value | 额定供电煤耗试验值 | rated coal consumption test value | rated coal consumption test value | 额定供电煤耗试验值 | 手填 |  | 400 | 200 | g/kWh |  |  | rated_coal_consumption_test_value | 额定供电煤耗试验值 | 288.72
| rated-coal-consumption-design-value | 额定煤耗设计值 | rated coal consumption design value | rated coal consumption design value | 额定煤耗设计值 | 手填 |  | 400 | 200 | g/kWh |  |  | rated_coal_consumption_design_value | 额定煤耗设计值 | 289.22
| rated-coal-consumption-assessment-value | 额定考核值 | rated coal consumption assessment value | rated coal consumption assessment value | 额定考核值 | 手填 |  | 400 | 200 | g/kWh |  |  | rated_coal_consumption_assessment_value | 额定考核值
| rated-coal-consumption-test-design-difference-value | 煤耗试验-设计比较 | rated coal consumption test-design difference value | rated coal consumption test-design difference value | 煤耗试验-设计比较 | 计算 |  | 400 | 200 | g/kWh |  |  | rated_coal_consumption_test_design_difference_value | 煤耗试验-设计比较 | =L5-L6
| annual-supervision-monthly-report-data | 年度监督月报数据 | annual supervision monthly report data | Annual supervision monthly report data | 年度监督月报数据 | 计算 |  |  |  | g/kWh |  |  | annual_supervision_monthly_report_data | 年度监督月报数据 | 2017.10～2018.9
| annual-average-load-rate | 年平均负荷率 | annual average load rate | Annual average load rate | 年平均负荷率 | 计算 |  | 40 | 100 | g/kWh | 61.34% |  | annual_average_load_rate | 年平均负荷率 | 各月负荷率*电量/(各月电量和)
| annual-average-coal-consumption | 年平均煤耗 | annual average coal consumption | Annual average coal consumption | 年平均煤耗 | 计算 |  | 400 | 200 | g/kWh | 308.86 |  | annual_average_coal_consumption | 年平均煤耗 | （各月电量/周期总电量）*各月煤耗
| -coal-consumption-industry-advanced | 煤耗行业先进值 | coal consumption industry advanced | Coal consumption Industry advanced | 煤耗行业先进值 | 手填 |  | 400 | 200 | g/kWh | 278.07 |  | _coal_consumption_industry_advanced | 煤耗行业先进值
| -coal-consumption-industry-average | 煤耗行业平均值 | coal consumption industry average | Coal consumption Industry average | 煤耗行业平均值 | 手填 |  | 400 | 200 | g/kWh | 287.92 |  | _coal_consumption_industry_average | 煤耗行业平均值
| -coal-consumption-crp-advanced | 煤耗华润先进值 | coal consumption crp advanced | Coal consumption Crp advanced | 煤耗华润先进值 | 手填 |  | 400 | 200 | g/kWh | 同类型NUM1 |  | _coal_consumption_crp_advanced | 煤耗华润先进值 | 266
| -coal-consumption-crp-average | 煤耗华润均值 | coal consumption crp average | Coal consumption Crp average | 煤耗华润均值 | 手填 |  | 400 | 200 | g/kWh | 同类型均值 |  | _coal_consumption_crp_average | 煤耗华润均值 | 266
|  | 0 | [11 empty] | 0
| factory-electricity-rate-test-value | 厂用电率-试验值 | factory electricity rate test value | Factory electricity rate test value | 厂用电率-试验值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate_test_value | 厂用电率-试验值 | 4.14
| factory-electricity-rate-assessment-value | 厂用电率-考核值 | factory electricity rate assessment value | Factory electricity rate assessment value | 厂用电率-考核值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate_assessment_value | 厂用电率-考核值 | 3.44
| factory-electricity-rate-design-value | 厂用电率-设计值 | factory electricity rate design value | Factory electricity rate design value | 厂用电率-设计值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate_design_value | 厂用电率-设计值 | 4.65
| factory-electricity-rate--monthly-report-data | 厂用电率-统计值 | factory electricity rate monthly report data | Factory electricity rate monthly report data | 厂用电率-统计值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate__monthly_report_data | 厂用电率-统计值 | 5.33
| factory-electricity-rate-industry-advanced | 厂用电率-行业先进值 | factory electricity rate industry advanced | Factory electricity rate industry advanced | 厂用电率-行业先进值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate_industry_advanced | 厂用电率-行业先进值 | 3
| factory-electricity-rate-industry-average | 厂用电率-行业均值 | factory electricity rate industry average | Factory electricity rate industry average | 厂用电率-行业均值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate_industry_average | 厂用电率-行业均值 | 3
| factory-electricity-rate-crp-advanced | 厂用电率-华润先进值 | factory electricity rate crp advanced | Factory electricity rate CRP advanced | 厂用电率-华润先进值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate_crp_advanced | 厂用电率-华润先进值 | 3
| factory-electricity-rate-crp-average | 厂用电率-华润均值 | factory electricity rate crp average | Factory electricity rate CRP average | 厂用电率-华润均值 | 手填 |  | 0 | 20 | % |  |  | factory_electricity_rate_crp_average | 厂用电率-华润均值 | 3
|  | 0 |  |  |  | 手填 | [7 empty] | 0
| annual-fuel-consumption | 油耗 | annual fuel consumption | Annual fuel consumption | 油耗 | 计算 |  | 0 | 1000 | t/a |  |  | annual_fuel_consumption | 油耗 | 月油耗求和
|  | 油耗行业平均值 | [10 empty] | annual_fuel_consumption_industry_average | 油耗行业平均值
| annual-water-consumption | 水耗 | annual water consumption | Annual water consumption | 水耗 | 计算 |  | 0 | 5 | kg/kWh |  |  | annual_water_consumption | 水耗 | 月水耗*月电量/总电量
|  | 水耗行业平均值 | [10 empty] | annual_water_consumption_industry_average | 水耗行业平均值
|  | 0 | [11 empty] | 0
| test-curve-coal-consumption | 试验特性曲线煤耗 | test curve coal consumption | Test curve coal consumption | 试验特性曲线煤耗 | [7 empty] | test_curve_coal_consumption | 试验特性曲线煤耗 | 308.25
| test-curve-coal-consumption-correction | 试验特性曲线煤耗修正 | test curve coal consumption correction | Test curve coal consumption correction | 试验特性曲线煤耗修正 | [7 empty] | test_curve_coal_consumption_correction | 试验特性曲线煤耗修正 | 308.65
| coal-consumption-adaptation-difference | 煤耗适配差值 | coal consumption adaptation difference | Coal consumption adaptation difference | 煤耗适配差值 | 计算 |  | 0 | 10 | g/kWh |  |  | coal_consumption_adaptation_difference | 煤耗适配差值 | #VALUE!
|  | 0 | [11 empty] | 0
| heat-rate-test | 热耗率 | heat rate test | Heat rate test | 热耗率 | 手填 |  | 4000 | 9000 | kJ/kWh |  |  | heat_rate_test | 热耗率 | 7620.1
| heat-rate-design | 设计热耗率 | heat rate design | Heat rate design | 设计热耗率 | 手填 |  | 4000 | 9000 | kJ/kWh |  |  | heat_rate_design | 设计热耗率 | 7434
| heat-rate-assessment | 考核热耗率 | heat rate assessment | Heat rate assessment | 考核热耗率 | 手填 |  | 4000 | 9000 | kJ/kWh |  |  | heat_rate_assessment | 考核热耗率 | 7478.81
|  | 0 | [11 empty] | 0
| boiler-efficiency | 锅炉效率 | boiler efficiency | Boiler efficiency | 锅炉效率 | 手填 |  | 85 | 100 | % |  |  | boiler_efficiency | 锅炉效率 | 94.889
| boiler-efficiency-design | 设计锅炉效率 | boiler efficiency design | Boiler efficiency design | 设计锅炉效率 | 手填 |  | 85 | 100 | % |  |  | boiler_efficiency_design | 设计锅炉效率 | 92.909
| boiler-efficiency-assessment | 考核锅炉效率 | boiler efficiency assessment | Boiler efficiency assessment | 考核锅炉效率 | 手填 |  | 85 | 100 | % |  |  | boiler_efficiency_assessment | 考核锅炉效率 | 94.48
| exhaust-temperature | 排烟温度 | exhaust temperature | exhaust temperature | 排烟温度 | 手填 |  | 100 | 150 | ℃ |  |  | exhaust_temperature | 排烟温度
| exhaust-temperature-design | 排烟温度设计值 | exhaust temperature design | exhaust temperature design | 排烟温度设计值 | 手填 |  | 100 | 150 | ℃ |  |  | exhaust_temperature_design | 排烟温度设计值
| fly-ash-carbon-content | 飞灰含碳量 | fly ash carbon content | Fly ash carbon content | 飞灰含碳量 | 手填 |  | 0 | 20 | % |  |  | fly_ash_carbon_content | 飞灰含碳量
| slag-carbon-content | 炉渣含碳量 | slag carbon content | Slag carbon content | 炉渣含碳量 | 手填 |  | 0 | 20 | % |  |  | slag_carbon_content | 炉渣含碳量
| smoke-exhaust-co | CO | smoke exhaust co | Smoke exhaust CO | CO | 手填 |  | 0 | 800 | % |  |  | smoke_exhaust_co | 烟气CO
| a-side-air-leakage-rate | A侧漏风率 | a side air leakage rate | A side air leakage rate | A侧漏风率 | 手填 |  | 0 | 20 | % |  |  | a_side_air_leakage_rate | A侧漏风率
[13 empty] | a_side_air_leakage_rate_design | A侧漏风率设计值
| b-side-air-leakage-rate | B侧漏风率 | b side air leakage rate | B side air leakage rate | B侧漏风率 | 手填 |  | 0 | 20 | % |  |  | b_side_air_leakage_rate | B侧漏风率
[13 empty] | b_side_air_leakage_rate_design | B侧漏风率设计值
| a-side-air-preherter-differential-pressure | A侧差压 | a side air preherter differential pressure | A side air preherter differential pressure | A侧差压 | 手填 |  | 0 | 10000 | Pa |  |  | a_side_air_preherter_differential_pressure | A侧差压
[13 empty] | a_side_air_preherter_differential_pressure_design | A侧差压设计值
| b-side-air-preherter-differential-pressure | B侧差压 | b side air preherter differential pressure | B side air preherter differential pressure | B侧差压 | 手填 |  | 0 | 10000 | Pa |  |  | b_side_air_preherter_differential_pressure | B侧差压
[13 empty] | b_side_air_preherter_differential_pressure_design | B侧差压设计值
| main-steam-temperature | 主汽温度 | main steam temperature | Main steam temperature | 主汽温度 | 手填 |  | 400 | 650 | ℃ |  |  | main_steam_temperature | 主汽温度
| reheat-temperature | 再热温度 | reheat temperature | Reheat temperature | 再热温度 | 手填 |  | 400 | 650 | ℃ |  |  | reheat_temperature | 再热温度
| hp-cylinder-efficiency | 高缸效率 | hp cylinder efficiency | HP cylinder efficiency | 高缸效率 | 手填 |  | 50 | 100 | % |  |  | hp_cylinder_efficiency | 高缸效率
| ip-cylinder-efficiency | 中缸效率 | ip cylinder efficiency | IP cylinder efficiency | 中缸效率 | 手填 |  | 50 | 100 | % |  |  | ip_cylinder_efficiency | 中缸效率
| #1-high-pressure-heater-upper-terminal-difference-temperature | #1高加上端差 | #1 high pressure heater upper terminal difference temperature | #1 high pressure heater upper terminal difference temperature | #1高加上端差 | 手填 |  | -5 | 50 | ℃ |  |  | #1_high_pressure_heater_upper_terminal_difference_temperature | #1高加上端差
[13 empty] | #1_high_pressure_heater_upper_terminal_difference_temperature_design | #1高加上端差设计值
| #2-high-pressure-heater-upper-terminal-difference-temperature | #2高加上端差 | #2 high pressure heater upper terminal difference temperature | #2 high pressure heater upper terminal difference temperature | #2高加上端差 | 手填 |  | -5 | 50 | ℃ |  |  | #2_high_pressure_heater_upper_terminal_difference_temperature | #2高加上端差
[13 empty] | #2_high_pressure_heater_upper_terminal_difference_temperature_design | #2高加上端差设计值
| #3-high-pressure-heater-upper-terminal-differencel-temperature | #3高加上端差 | #3 high pressure heater upper terminal differencel temperature | #3 high pressure heater upper terminal differencel temperature | #3高加上端差 | 手填 |  | -5 | 50 | ℃ |  |  | #3_high_pressure_heater_upper_terminal_differencel_temperature | #3高加上端差
[13 empty] | #3_high_pressure_heater_upper_terminal_differencel_temperature_design | #3高加上端差设计值
|  | 0 | [11 empty] | 0
| table-column-name- | 项目 | table column name | Table Column name | 项目 | [7 empty] | table_column_name_ | 项目 | 项目
| generator-power | 发电机功率 | generator power | Generator power | 发电机功率 | 手填 |  | 200 | 1100 | kW |  |  | generator_power | 发电机功率 | 发电机功率
| main-steam-pressure | 主汽压力 | main steam pressure | Main steam pressure | 主汽压力 | 手填 |  | 5 | 40 | MPa |  |  | main_steam_pressure | 主汽压力 | 主汽压力
| main-steam-temperature | 主汽温度 | main steam temperature | Main steam temperature | 主汽温度 | 手填 |  | 300 | 700 | ℃ |  |  | main_steam_temperature | 主汽温度 | 主汽温度
| high-discharge-pressure | 高排压力 | high discharge pressure | High discharge pressure | 高排压力 | 手填 |  | 0 | 10 | MPa |  |  | high_discharge_pressure | 高排压力 | 高排压力
| hp-exhaust-steam-temperature | 高排温度 | hp exhaust steam temperature | HP Exhaust steam temperature | 高排温度 | 手填 |  | 100 | 500 | ℃ |  |  | hp_exhaust_steam_temperature | 高排温度 | 高排温度
| reheating-pressure | 再热压力 | reheating pressure | Reheating pressure | 再热压力 | 手填 |  | 0 | 10 | MPa |  |  | reheating_pressure | 再热压力 | 再热压力
| reheat-temperature | 再热温度 | reheat temperature | Reheat temperature | 再热温度 | 手填 |  | 300 | 700 | ℃ |  |  | reheat_temperature | 再热温度 | 再热温度
| intermediate-pressure | 中排汽压力 | intermediate pressure | Intermediate pressure | 中排汽压力 | 手填 |  | 0 | 5 | MPa |  |  | intermediate_pressure | 中排汽压力 | 中排汽压力
| ip-exhaust-steam-temperature | 中排汽温度 | ip exhaust steam temperature | IP Exhaust steam temperature | 中排汽温度 | 手填 |  | 100 | 400 | ℃ |  |  | ip_exhaust_steam_temperature | 中排汽温度 | 中排汽温度
| lp-exhaust-pressure | 排汽压力 | lp exhaust pressure | LP Exhaust pressure | 排汽压力 | 手填 |  | 0 | 20 | kPa |  |  | lp_exhaust_pressure | 排汽压力 | 排汽压力
| feed-water-temperature | 给水温度 | feed water temperature | Feed water temperature | 给水温度 | 手填 |  | 100 | 400 | ℃ |  |  | feed_water_temperature | 给水温度 | 给水温度
| hp-cylinder-efficiency | 高压缸效率 | hp cylinder efficiency | HP cylinder efficiency | 高压缸效率 | 手填 |  | 0 | 100 | % |  |  | hp_cylinder_efficiency | 高压缸效率 | 高压缸效率
| ip-cylinder-efficiency | 中压缸效率 | ip cylinder efficiency | IP cylinder efficiency | 中压缸效率 | 手填 |  | 0 | 100 | % |  |  | ip_cylinder_efficiency | 中压缸效率 | 中压缸效率
| heat-rate-test | 试验热耗率 | heat rate test | Heat rate test | 试验热耗率 | 手填 |  | 4000 | 9000 | kJ/kWh |  |  | heat_rate_test | 试验热耗率 | 试验热耗率
| heat-rate-test-correction | 修正后热耗率 | heat rate test correction | Heat rate test Correction | 修正后热耗率 | 手填 |  | 4000 | 9000 | kJ/kWh |  |  | heat_rate_test_correction | 修正后热耗率 | 修正后热耗率
| generator-power-correction | 修正后发电机功率 | generator power correction | Generator power Correction | 修正后发电机功率 | 手填 |  | 200 | 1100 | kW |  |  | generator_power_correction | 修正后发电机功率 | 修正后发电机功率
| turbine-design-parameter | 机侧设计值 | turbine design parameter | Turbine design parameter | 机侧设计值 | 手填 | [6 empty] | turbine_design_parameter | 机侧设计值 | 设计值
| turbine-test-parameter | 机侧试验值 | turbine test parameter | Turbine test parameter | 机侧试验值 | 手填 | [6 empty] | turbine_test_parameter | 机侧试验值 | 试验值
|  | 0 | [11 empty] | 0
| exhaust-temperature | 排烟温度 | exhaust temperature | exhaust temperature | 排烟温度 | 手填 |  | 100 | 150 | ℃ |  |  | exhaust_temperature | 排烟温度 | 排烟温度
| exhaust-temperature-correction | 排烟温度（修正后） | exhaust temperature correction | exhaust temperature Correction | 排烟温度（修正后） | 手填 |  | 100 | 150 | ℃ |  |  | exhaust_temperature_correction | 排烟温度（修正后） | 排烟温度（修正后）
| fly-ash-carbon-content | 飞灰含碳量 | fly ash carbon content | Fly ash carbon content | 飞灰含碳量 | 手填 |  | 0 | 20 | % |  |  | fly_ash_carbon_content | 飞灰含碳量 | 飞灰含碳量
| slag-carbon-content | 炉渣含碳量 | slag carbon content | Slag carbon content | 炉渣含碳量 | 手填 |  | 0 | 20 | % |  |  | slag_carbon_content | 炉渣含碳量 | 炉渣含碳量
| smoke-exhaust-co | 空预器出口CO含量 | smoke exhaust co | Smoke exhaust CO | 空预器出口CO含量 | 手填 |  | 0 | 1000 | % |  |  | smoke_exhaust_co | 空预器出口CO含量 | 空预器出口CO含量
| exhaust-heat-loss-q2 | 排烟热损失q2 | exhaust heat loss q2 | Exhaust heat loss q2 | 排烟热损失q2 | 手填 |  | 0 | 20 | % |  |  | exhaust_heat_loss_q2 | 排烟热损失q2 | 排烟热损失q2
| gas-incomplete-combustion-heat-loss-q3 | 气体未完全燃烧热损失q3 | gas incomplete combustion heat loss q3 | Gas incomplete combustion heat loss q3 | 气体未完全燃烧热损失q3 | 手填 |  | 0 | 20 | % |  |  | gas_incomplete_combustion_heat_loss_q3 | 气体未完全燃烧热损失q3 | 气体未完全燃烧热损失q3
| solid-incomplete-combustion-heat-loss-q4 | 固体未完全燃烧热损失q4 | solid incomplete combustion heat loss q4 | Solid incomplete combustion heat loss q4 | 固体未完全燃烧热损失q4 | 手填 |  | 0 | 20 | % |  |  | solid_incomplete_combustion_heat_loss_q4 | 固体未完全燃烧热损失q4 | 固体未完全燃烧热损失q4
| boiler-heat-loss-q5 | 锅炉散热损失q5 | boiler heat loss q5 | Boiler heat loss q5 | 锅炉散热损失q5 | 手填 |  | 0 | 20 | % |  |  | boiler_heat_loss_q5 | 锅炉散热损失q5 | 锅炉散热损失q5
| heat-loss-of-ash-and-slag-q6 | 灰、渣物理显热损失q6 | heat loss of ash and slag q6 | heat loss of ash and slag q6 | 灰、渣物理显热损失q6 | 手填 |  | 0 | 20 | % |  |  | heat_loss_of_ash_and_slag_q6 | 灰、渣物理显热损失q6 | 灰、渣物理显热损失q6
| other-heat-loss-qoth | 其他热损失qoth | other heat loss qoth | Other heat loss qoth | 其他热损失qoth | 手填 |  | 0 | 20 | % |  |  | other_heat_loss_qoth | 其他热损失qoth | 其他热损失qoth
| percentage-of-external-heat-and-fuel-low-heat-qex | 外来热量与燃料低位发热量的百分比qex | percentage of external heat and fuel low heat qex | Percentage of external heat and fuel low heat qex | 外来热量与燃料低位发热量的百分比qex | 手填 |  | 0 | 100 | % |  |  | percentage_of_external_heat_and_fuel_low_heat_qex | 外来热量与燃料低位发热量的百分比qex | 外来热量与燃料低位发热量的百分比qex
| boiler-efficiency | 换算到保证条件下锅炉热效率η | boiler efficiency | Boiler efficiency | 换算到保证条件下锅炉热效率η | 手填 |  | 0 | 100 | % |  |  | boiler_efficiency | 换算到保证条件下锅炉热效率η | 换算到保证条件下锅炉热效率η
| a-side-air-leakage-rate | A侧漏风率 | a side air leakage rate | A side air leakage rate | A侧漏风率 | 手填 |  | 0 | 20 | % |  |  | a_side_air_leakage_rate | A侧漏风率 | A侧漏风率
A侧漏风率设计值
| b-side-air-leakage-rate | B侧漏风率 | b side air leakage rate | B side air leakage rate | B侧漏风率 | 手填 |  | 0 | 20 | % |  |  | b_side_air_leakage_rate | B侧漏风率 | B侧漏风率
| a-side-air-preherter-differential-pressure | A侧差压 | a side air preherter differential pressure | A side air preherter differential pressure | A侧差压 | 手填 |  | 0 | 10000 | Pa |  |  | a_side_air_preherter_differential_pressure | A侧差压 | A侧差压
| b-side-air-preherter-differential-pressure | B侧差压 | b side air preherter differential pressure | B side air preherter differential pressure | B侧差压 | 手填 |  | 0 | 10000 | Pa |  |  | b_side_air_preherter_differential_pressure | B侧差压 | B侧差压
|  | 0 | [11 empty] | 0
| generator-power | 机组负荷 | generator power | Generator power | 机组负荷 | 手填 |  | 0 | 11000 | MW |  |  | generator_power | 机组负荷 | 机组负荷
| flue-gas-flow | 烟气流量（标干、6%O2） | flue gas flow | Flue gas flow | 烟气流量（标干、6%O2） | 手填 |  | 1000000 | 3000000 | m3/h |  |  | flue_gas_flow | 烟气流量（标干、6%O2） | 烟气流量（标干、6%O2）
| imported-smoke-so2-content | 原烟气SO2浓度 | imported smoke so2 content | Imported smoke SO2 content | 原烟气SO2浓度 | 手填 |  | 0 | 10000 | mg/m3 |  |  | imported_smoke_so2_content | 原烟气SO2浓度 | 原烟气SO2浓度
| exported-smoke-so2-content | 总排口SO2浓度 | exported smoke so2 content | Exported smoke SO2 content | 总排口SO2浓度 | 手填 |  | 0 | 100 | mg/m3 |  |  | exported_smoke_so2_content | 总排口SO2浓度 | 总排口SO2浓度
| desulfurization-efficiency | 脱硫效率 | desulfurization efficiency | Desulfurization efficiency | 脱硫效率 | 手填 |  | 50 | 100 | % |  |  | desulfurization_efficiency | 脱硫效率 | 脱硫效率
| running-circulating-pump | 循环泵投运数量 | running circulating pump | Running circulating pump | 循环泵投运数量 | 手填 |  | 0 | 10 | 台 |  |  | running_circulating_pump | 循环泵投运数量 | 循环泵投运数量
| desulfurization-resistance | 脱硫系统阻力 | desulfurization resistance | Desulfurization resistance | 脱硫系统阻力 | 手填 |  | 0 | 10000 | Pa |  |  | desulfurization_resistance | 脱硫系统阻力 | 脱硫系统阻力
|  | 0 |  |  |  | 手填 | [7 empty] | 0
| scr-imported-smoke-nox-content | 脱硝前烟气NOX浓度 | scr imported smoke nox content | SCR Imported smoke NOX content | 脱硝前烟气NOX浓度 | 手填 |  | 0 | 2000 | mg/m3 |  |  | scr_imported_smoke_nox_content | 脱硝前烟气NOX浓度 | 脱硝前烟气NOX浓度
| scr-exported-smoke-nox-content | 脱硝后烟气NOx浓度 | scr exported smoke nox content | SCR Exported smoke NOX content | 脱硝后烟气NOx浓度 | 手填 |  | 0 | 100 | mg/m3 |  |  | scr_exported_smoke_nox_content | 脱硝后烟气NOx浓度 | 脱硝后烟气NOx浓度
| scr-nox-content-difference | 脱硝后烟气NOx浓度分布偏差 | scr nox content difference | SCR NOX content difference | 脱硝后烟气NOx浓度分布偏差 | 手填 |  | 0 | 200 | % |  |  | scr_nox_content_difference | 脱硝后烟气NOx浓度分布偏差 | 脱硝后烟气NOx浓度分布偏差
| denitration-efficiency | 脱硝效率 | denitration efficiency | Denitration efficiency | 脱硝效率 | 手填 |  | 0 | 100 | % |  |  | denitration_efficiency | 脱硝效率 | 脱硝效率
| ammonia-escape- | 氨逃逸浓度 | ammonia escape | Ammonia escape | 氨逃逸浓度 | 手填 |  | 0 | 50 | ppm |  |  | ammonia_escape_ | 氨逃逸浓度 | 氨逃逸浓度
|  | 0 | [11 empty] | 0
| high-pressure-heater-terminal-difference-temperature | 高压加热器上端差 | high pressure heater terminal difference temperature | High pressure heater terminal difference temperature | 高压加热器上端差 | 手填 | [6 empty] | high_pressure_heater_terminal_difference_temperature | 高压加热器上端差 | 高压加热器上端差
| lp-cylinder-efficiency-thermal-system-leakage | 低压缸效率、热力系统严密性 | lp cylinder efficiency thermal system leakage | LP cylinder efficiency thermal system leakage | 低压缸效率、热力系统严密性 | 手填 | [6 empty] | lp_cylinder_efficiency_thermal_system_leakage | 低压缸效率、热力系统严密性 | 低压缸效率、热力系统严密性
| other-factors | 其他影响因素 | other factors | other factors | 其他影响因素 | 手填 | [6 empty] | other_factors | 其他影响因素 | 其他影响因素
| sum | 合计 | sum | sum | 合计 | 手填 | [6 empty] | sum | 合计 | 合计
| small-indicator-design-value | 小指标设计值 | small indicator design value | Small indicator design value | 小指标设计值 | 手填 | [6 empty] | small_indicator_design_value | 小指标设计值 | 设计值
| small-indicator-test-value | 小指标试验值 | small indicator test value | Small indicator test value | 小指标试验值 | 手填 | [6 empty] | small_indicator_test_value | 小指标试验值 | 试验值
| small-indicator-different-value | 小指标差值 | small indicator different value | Small indicator different value | 小指标差值 | 手填 | [6 empty] | small_indicator_different_value | 小指标差值 | 差值
| small-indicator-increased-coal-consumption | 小指标煤耗上升 | small indicator increased coal consumption | Small indicator Increased coal consumption | 小指标煤耗上升 | 手填 | [6 empty] | small_indicator_increased_coal_consumption | 小指标煤耗上升 | 煤耗上升
| small-indicator-reduced-coal-consumption | 小指标煤耗下降 | small indicator reduced coal consumption | Small indicator reduced coal consumption | 小指标煤耗下降 | 手填 | [6 empty] | small_indicator_reduced_coal_consumption | 小指标煤耗下降 | 煤耗下降
| controllable/uncontrollable-factors | 可控/不可控因素 | controllable/uncontrollable factors | Controllable/Uncontrollable factors | 可控/不可控因素 | 手填 | [6 empty] | controllable/uncontrollable_factors | 可控/不可控因素 | 可控/不可控因素
|  | 0 | [11 empty] | 0
| monthly-load-rate | 月报负荷率 | monthly load rate | Monthly load rate | 月报负荷率 | 手填 |  | 40 | 100 | % |  |  | monthly_load_rate | 月报负荷率 | 负荷率
| monthly--coal-consumption-fa | 月报发电煤耗 | monthly coal consumption fa | Monthly coal consumption fa | 月报发电煤耗 | 手填 |  | 200 | 400 | g/kWh |  |  | monthly__coal_consumption_fa | 月报发电煤耗 | 发电煤耗
| monthly--coal-consumption | 月报供电煤耗 | monthly coal consumption | Monthly coal consumption | 月报供电煤耗 | 手填 |  | 200 | 400 |  |  |  | monthly__coal_consumption | 月报供电煤耗 | 供电煤耗
| monthly-factory-electricity-rate | 月报厂用电率 | monthly factory electricity rate | Monthly Factory electricity rate | 月报厂用电率 | 手填 |  | 0 | 20 | % |  |  | monthly_factory_electricity_rate | 月报厂用电率 | 厂用电率
| monthly-vacuum-degree | 月报真空度 | monthly vacuum degree | Monthly Vacuum degree | 月报真空度 | 手填 |  | 0 | 100 | % |  |  | monthly_vacuum_degree | 月报真空度 | 真空度
| monthly-report-main-steam-pressure | 月报主汽压力 | monthly report main steam pressure | Monthly report main steam pressure | 月报主汽压力 | 手填 | [6 empty] | monthly_report_main_steam_pressure | 月报主汽压力 | 主汽压力
| monthly-report-main-steam-temperature | 月报主汽温度 | monthly report main steam temperature | Monthly report main steam temperature | 月报主汽温度 | 手填 | [6 empty] | monthly_report_main_steam_temperature | 月报主汽温度 | 主汽温度
| monthly-reheating-pressure | 月报再热压力 | monthly reheating pressure | Monthly reheating pressure | 月报再热压力 | 手填 | [6 empty] | monthly_reheating_pressure | 月报再热压力 | 再热压力
| monthly-reheat-temperature | 月报再热温度 | monthly reheat temperature | Monthly reheat temperature | 月报再热温度 | 手填 | [6 empty] | monthly_reheat_temperature | 月报再热温度 | 再热温度
| monthly-hours-of-use | 月报利用小时数 | monthly hours of use | Monthly Hours of use | 月报利用小时数 | 手填 |  | 0 | 5000 | h |  |  | monthly_hours_of_use | 月报利用小时数 | 利用小时数
| monthly-circulating-pump-unit-consumption | 月报循环水泵耗电率 | monthly circulating pump unit consumption | Monthly Circulating pump unit consumption | 月报循环水泵耗电率 | 手填 |  | 0 | 5 | % |  |  | monthly_circulating_pump_unit_consumption | 月报循环水泵耗电率 | 循环水泵耗电率
| monthly-condensate-pump-unit-consumption | 月报凝结水泵耗电率 | monthly condensate pump unit consumption | Monthly Condensate pump unit consumption | 月报凝结水泵耗电率 | 手填 |  | 0 | 5 | % |  |  | monthly_condensate_pump_unit_consumption | 月报凝结水泵耗电率 | 凝结水泵耗电率
| monthly-front-pump-unit-consumption | 月报前置泵耗电率 | monthly front pump unit consumption | Monthly Front pump unit consumption | 月报前置泵耗电率 | 手填 |  | 0 | 5 | % |  |  | monthly_front_pump_unit_consumption | 月报前置泵耗电率 | 前置泵耗电率
|  | 0 | [11 empty] | 0
| monthly-report-boiler-efficiency | 月报锅炉效率 | monthly report boiler efficiency | Monthly report boiler efficiency | 月报锅炉效率 | 手填 | [6 empty] | monthly_report_boiler_efficiency | 月报锅炉效率 | 锅炉效率
| monthly-report-exhaust-temperature | 月报排烟温度 | monthly report exhaust temperature | Monthly report exhaust temperature | 月报排烟温度 | 手填 | [6 empty] | monthly_report_exhaust_temperature | 月报排烟温度 | 排烟温度
| monthly-cold-air-temperature | 月报冷风温度 | monthly cold air temperature | Monthly cold air temperature | 月报冷风温度 | 手填 | [6 empty] | monthly_cold_air_temperature | 月报冷风温度 | 冷风温度
| monthly-report-fly-ash-carbon-content | 月报飞灰含碳量 | monthly report fly ash carbon content | Monthly report fly ash carbon content | 月报飞灰含碳量 | 手填 | [6 empty] | monthly_report_fly_ash_carbon_content | 月报飞灰含碳量 | 飞灰含碳量
| monthly-report-slag-carbon-content | 月报炉渣含碳量 | monthly report slag carbon content | Monthly report slag carbon content | 月报炉渣含碳量 | 手填 | [6 empty] | monthly_report_slag_carbon_content | 月报炉渣含碳量 | 炉渣含碳量
| monthly-air-leakage-rate | 月报空预器漏风率 | monthly air leakage rate | Monthly air leakage rate | 月报空预器漏风率 | 手填 | [6 empty] | monthly_air_leakage_rate | 月报空预器漏风率 | 空预器漏风率
| monthly-air-preherter-differential-pressure | 月报空预器烟气差压 | monthly air preherter differential pressure | Monthly air preherter differential pressure | 月报空预器烟气差压 | 手填 |  | 0 | 10000 | Pa |  |  | monthly_air_preherter_differential_pressure | 月报空预器烟气差压 | 空预器烟气差压
| monthly-fuel-consumption | 月报油耗 | monthly fuel consumption | Monthly fuel consumption | 月报油耗 | 手填 |  | 0 | 500 | t |  |  | monthly_fuel_consumption | 月报油耗 | 油耗
| monthly-superheater-desuperheating-water | 月报过热减温水流量 | monthly superheater desuperheating water | Monthly Superheater desuperheating water | 月报过热减温水流量 | 手填 |  | 0 | 300 | t/h |  |  | monthly_superheater_desuperheating_water | 月报过热减温水流量 | 过热减温水流量
| monthly-reheater-desuperheating-water | 月报再热减温水流量 | monthly reheater desuperheating water | Monthly Reheater desuperheating water | 月报再热减温水流量 | 手填 |  | 0 | 300 | t/h |  |  | monthly_reheater_desuperheating_water | 月报再热减温水流量 | 再热减温水流量
| monthly-coal-mill | 月报磨煤机耗电率 | monthly coal mill | Monthly Coal mill | 月报磨煤机耗电率 | 手填 |  | 0 | 5 | % |  |  | monthly_coal_mill | 月报磨煤机耗电率 | 磨煤机耗电率
| monthly--primary-fan-unit-consumption | 月报一次风机耗电率 | monthly primary fan unit consumption | Monthly Primary Fan unit consumption | 月报一次风机耗电率 | 手填 |  | 0 | 5 | % |  |  | monthly__primary_fan_unit_consumption | 月报一次风机耗电率 | 一次风机耗电率
| monthly--blower-unit-consumption | 月报送风机耗电率 | monthly blower unit consumption | Monthly Blower unit consumption | 月报送风机耗电率 | 手填 |  | 0 | 5 | % |  |  | monthly__blower_unit_consumption | 月报送风机耗电率 | 送风机耗电率
| monthly--fan-unit-consumption | 月报引风机耗电率 | monthly fan unit consumption | Monthly Fan unit consumption | 月报引风机耗电率 | 手填 |  | 0 | 5 | % |  |  | monthly__fan_unit_consumption | 月报引风机耗电率 | 引风机耗电率
|  | 0 | [5 empty] | 0 | 5 | % |  |  |  | 0
月报发电取水量
中电联取水平均值
[10 empty] | t/tSO2 |  |  |  | 石灰石单耗
石灰石单耗评级
[10 empty] | t/tNOx |  |  |  | 氮单耗
氮单耗评级
| category | 类别 | category | category | 类别 | 手填 | [6 empty] | category | 类别 | 类别
| operation-optimization | 运行优化 | operation optimization | Operation optimization | 运行优化 | 手填 |  |  |  | g/kWh |  |  | operation_optimization | 运行优化 | 运行优化
| maintenance-technical-reform | 检修技改 | maintenance technical reform | Maintenance technical reform | 检修技改 | 手填 |  |  |  | g/kWh |  |  | maintenance_technical_reform | 检修技改 | 检修、技改
| other | 其他 | other | Other | 其他 | 手填 |  |  |  | g/kWh |  |  | other | 其他 | 其他
| incremental-energy-saving | 增加节能潜力 | incremental energy saving | Incremental energy saving | 增加节能潜力 | 手填 |  |  |  | g/kWh |  |  | incremental_energy_saving | 增加节能潜力 | 增加节能潜力
| reduced-coal-consumption-1 | 降低煤耗1 | reduced coal consumption 1 | reduced coal consumption 1 | 降低煤耗1 | 手填 |  |  |  | g/kWh |  |  | reduced_coal_consumption_1 | 降低煤耗1 | 降低煤耗
| reduced-coal-consumption-2 | 降低煤耗2 | reduced coal consumption 2 | reduced coal consumption 2 | 降低煤耗2 | 手填 |  |  |  | g/kWh |  |  | reduced_coal_consumption_2 | 降低煤耗2 | 降低煤耗

## Sheet2
锅炉效率 | 排烟温度 | 冷风温度 | 飞灰含碳量 | 炉渣含碳量 | 空预器漏风率 | 空预器烟气差压
油耗 | 过热减温水流量 | 再热减温水流量 | 磨煤机耗电率 | 一次风机耗电率 | 送风机耗电率 | 引风机耗电率
锅炉效率
排烟温度
冷风温度
飞灰含碳量
炉渣含碳量
空预器漏风率
空预器烟气差压
油耗
过热减温水流量
再热减温水流量
磨煤机耗电率
一次风机耗电率
送风机耗电率
引风机耗电率

## Sheet1
name | 中文名称
power-plant-full-name | 电厂全称
power-plant-abbreviated-name | 电厂简称
unit-nums | 机组号
0
rated-coal-consumption-test-value | 额定供电煤耗试验值
rated-coal-consumption-design-value | 额定煤耗设计值
rated-coal-consumption-assessment-value | 额定考核值
rated-coal-consumption-test-design-difference-value | 煤耗试验-设计比较
annual-supervision-monthly-report-data | 年度监督月报数据
annual-average-load-rate | 年平均负荷率
annual-average-coal-consumption | 年平均煤耗
-coal-consumption-industry-advanced | 煤耗行业先进值
-coal-consumption-industry-average | 煤耗行业平均值
-coal-consumption-crp-advanced | 煤耗华润先进值
-coal-consumption-crp-average | 煤耗华润均值
0
factory-electricity-rate-test-value | 厂用电率-试验值
factory-electricity-rate-assessment-value | 厂用电率-考核值
factory-electricity-rate-design-value | 厂用电率-设计值
factory-electricity-rate--monthly-report-data | 厂用电率-统计值
factory-electricity-rate-industry-advanced | 厂用电率-行业先进值
factory-electricity-rate-industry-average | 厂用电率-行业均值
factory-electricity-rate-crp-advanced | 厂用电率-华润先进值
factory-electricity-rate-crp-average | 厂用电率-华润均值
0
annual-fuel-consumption | 油耗
annual-water-consumption | 水耗
0
test-curve-coal-consumption | 试验特性曲线煤耗
test-curve-coal-consumption-correction | 试验特性曲线煤耗修正
coal-consumption-adaptation-difference | 煤耗适配差值
0
heat-rate-test | 热耗率
heat-rate-design | 设计热耗率
heat-rate-assessment | 考核热耗率
0
boiler-efficiency | 锅炉效率
boiler-efficiency-design | 设计锅炉效率
boiler-efficiency-assessment | 考核锅炉效率
exhaust-temperature | 排烟温度
exhaust-temperature-design | 排烟温度设计值
fly-ash-carbon-content | 飞灰含碳量
slag-carbon-content | 炉渣含碳量
smoke-exhaust-co | CO
a-side-air-leakage-rate | A侧漏风率
b-side-air-leakage-rate | B侧漏风率
a-side-air-preherter-differential-pressure | A侧差压
b-side-air-preherter-differential-pressure | B侧差压
main-steam-temperature | 主汽温度
reheat-temperature | 再热温度
hp-cylinder-efficiency | 高缸效率
ip-cylinder-efficiency | 中缸效率
#1-high-pressure-heater-upper-terminal-difference-temperature | #1高加上端差
#2-high-pressure-heater-upper-terminal-difference-temperature | #2高加上端差
#3-high-pressure-heater-upper-terminal-differencel-temperature | #3高加上端差
0
table-column-name- | 项目
generator-power | 发电机功率
main-steam-pressure | 主汽压力
main-steam-temperature | 主汽温度
high-discharge-pressure | 高排压力
hp-exhaust-steam-temperature | 高排温度
reheating-pressure | 再热压力
reheat-temperature | 再热温度
intermediate-pressure | 中排汽压力
ip-exhaust-steam-temperature | 中排汽温度
lp-exhaust-pressure | 排汽压力
feed-water-temperature | 给水温度
hp-cylinder-efficiency | 高压缸效率
ip-cylinder-efficiency | 中压缸效率
heat-rate-test | 试验热耗率
heat-rate-test-correction | 修正后热耗率
generator-power-correction | 修正后发电机功率
turbine-design-parameter | 机侧设计值
turbine-test-parameter | 机侧试验值
0
exhaust-temperature | 排烟温度
exhaust-temperature-correction | 排烟温度（修正后）
fly-ash-carbon-content | 飞灰含碳量
slag-carbon-content | 炉渣含碳量
smoke-exhaust-co | 空预器出口CO含量
exhaust-heat-loss-q2 | 排烟热损失q2
gas-incomplete-combustion-heat-loss-q3 | 气体未完全燃烧热损失q3
solid-incomplete-combustion-heat-loss-q4 | 固体未完全燃烧热损失q4
boiler-heat-loss-q5 | 锅炉散热损失q5
heat-loss-of-ash-and-slag-q6 | 灰、渣物理显热损失q6
other-heat-loss-qoth | 其他热损失qoth
percentage-of-external-heat-and-fuel-low-heat-qex | 外来热量与燃料低位发热量的百分比qex
boiler-efficiency | 换算到保证条件下锅炉热效率η
a-side-air-leakage-rate | A侧漏风率
b-side-air-leakage-rate | B侧漏风率
a-side-air-preherter-differential-pressure | A侧差压
b-side-air-preherter-differential-pressure | B侧差压
0
generator-power | 机组负荷
flue-gas-flow | 烟气流量（标干、6%O2）
imported-smoke-so2-content | 原烟气SO2浓度
exported-smoke-so2-content | 总排口SO2浓度
desulfurization-efficiency | 脱硫效率
running-circulating-pump | 循环泵投运数量
desulfurization-resistance | 脱硫系统阻力
0
scr-imported-smoke-nox-content | 脱硝前烟气NOX浓度
scr-exported-smoke-nox-content | 脱硝后烟气NOx浓度
scr-nox-content-difference | 脱硝后烟气NOx浓度分布偏差
denitration-efficiency | 脱硝效率
ammonia-escape- | 氨逃逸浓度
0
high-pressure-heater-terminal-difference-temperature | 高压加热器上端差
lp-cylinder-efficiency-thermal-system-leakage | 低压缸效率、热力系统严密性
other-factors | 其他影响因素
sum | 合计
small-indicator-design-value | 小指标设计值
small-indicator-test-value | 小指标试验值
small-indicator-different-value | 小指标差值
small-indicator-increased-coal-consumption | 小指标煤耗上升
small-indicator-reduced-coal-consumption | 小指标煤耗下降
controllable/uncontrollable-factors | 可控/不可控因素
0
monthly-load-rate | 月报负荷率
monthly--coal-consumption-fa | 月报发电煤耗
monthly--coal-consumption | 月报供电煤耗
monthly-factory-electricity-rate | 月报厂用电率
monthly-vacuum-degree | 月报真空度
monthly-report-main-steam-pressure | 月报主汽压力
monthly-report-main-steam-temperature | 月报主汽温度
monthly-reheating-pressure | 月报再热压力
monthly-reheat-temperature | 月报再热温度
monthly-hours-of-use | 月报利用小时数
monthly-circulating-pump-unit-consumption | 月报循环水泵耗电率
monthly-condensate-pump-unit-consumption | 月报凝结水泵耗电率
monthly-front-pump-unit-consumption | 月报前置泵耗电率
0
monthly-report-boiler-efficiency | 月报锅炉效率
monthly-report-exhaust-temperature | 月报排烟温度
monthly-cold-air-temperature | 月报冷风温度
monthly-report-fly-ash-carbon-content | 月报飞灰含碳量
monthly-report-slag-carbon-content | 月报炉渣含碳量
monthly-air-leakage-rate | 月报空预器漏风率
monthly-air-preherter-differential-pressure | 月报空预器烟气差压
monthly-fuel-consumption | 月报油耗
monthly-superheater-desuperheating-water | 月报过热减温水流量
monthly-reheater-desuperheating-water | 月报再热减温水流量
monthly-coal-mill | 月报磨煤机耗电率
monthly--primary-fan-unit-consumption | 月报一次风机耗电率
monthly--blower-unit-consumption | 月报送风机耗电率
monthly--fan-unit-consumption | 月报引风机耗电率
0
category | 类别
operation-optimization | 运行优化
maintenance-technical-reform | 检修技改
other | 其他
incremental-energy-saving | 增加节能潜力
reduced-coal-consumption-1 | 降低煤耗1
reduced-coal-consumption-2 | 降低煤耗2